[Your logo]

Risk assessment and method statement

# Electrical work RAMS

Electrical installation, alteration and testing. Pre-filled with typical hazards, controls and sequence: edit it for this site.

Management of Health and Safety at Work Regulations 1999, regulation 3. Electricity at Work Regulations 1989.

| Detail | Entry |
| --- | --- |
| Project |  |
| Site address |  |
| Activity | Electrical installation, alteration and testing |
| RAMS reference |  |
| Contractor carrying out the work |  |
| Principal contractor |  |
| Prepared by |  |
| Approved by |  |
| Revision |  |
| Date |  |

Revision record. Reissue and rebrief when the sequence, the programme, the team or the conditions change.

| Rev | Date | What changed | By |
| --- | --- | --- | --- |

THE WORK

# The activity, the place and the people

## Scope of the activity

Installation of [containment, wiring, distribution boards and final circuits] to the drawings, alterations to existing circuits, and inspection and testing to BS 7671 with certification. Includes safe isolation of existing circuits in the work area. Live testing only as authorised in this RAMS. Not included: [list any exclusions].

## Location and access

Site access via [gate]. Points of isolation at [board or switch room ref], with keys held by [name]. Materials stored at [area]. Work in occupied areas from [time] to [time], with supply interruptions agreed with [client contact].

## Interfaces with other trades

Other trades in the same areas: [trades]. They are told before any circuit is isolated or restored. Isolations made by others, such as the building owner or another contractor, are confirmed in writing before work starts.

## Documents this RAMS relies on

Drawings and circuit schedules [ref]; existing installation records [ref]; asbestos register or survey [ref]. Utility drawings for any digging; construction phase plan; permit to work where required; BS 7671 certificates.

## Programme

| Start date | Duration | Working hours |
| --- | --- | --- |

## The team, and their competence

| Role | Name | Card, ticket or training needed | Contact |
| --- | --- | --- | --- |
| Electricians |  | ECS card for the grade of work, issued through the JIB, with apprentices and trainees supervised. |  |
| Supervisor |  | An experienced electrician on site, setting supervision by each person's competence and the work. |  |
| Testers |  | Competent in inspection and testing to BS 7671, and in the safe use of instruments under GS38. |  |
| Live work |  | Only people with the knowledge and experience for that task, named in the written authorisation. |  |
| Access equipment |  | PASMA training for mobile towers and IPAF for MEWPs. |  |
| Asbestos |  | Asbestos awareness training for everyone liable to disturb it. |  |

METHOD STATEMENT

# The sequence of work

The order the team will work in on the day, with the controls built into each stage. If the sequence changes on site, revise the RAMS and brief it again.

| Stage | What is done, and how | Controls at this stage | By |
| --- | --- | --- | --- |
| Before the day | Visit the site and confirm the scope, drawings, existing installation records, the asbestos information and the points of isolation. Agree any supply interruptions with the client and occupier. | Drawings and records on site; asbestos information checked; RAMS approved by the principal contractor. | Contracts manager |
| Arrival and briefing | Sign in, attend the site induction, then brief the team on this RAMS, the isolation procedure and the emergency arrangements. Check test equipment, locks and tools. | Briefing signed against this revision; ECS cards checked; voltage indicator and proving unit checked. | Supervisor |
| Identify the circuits | Identify every circuit and source of supply in the work area from drawings, labels and testing. Look for back-feeds, generators, solar inverters and batteries. | Labels never relied on alone; anything that cannot be identified is treated as live. | Electrician |
| Isolate and lock off | Switch off, then isolate at a lockable device. Fit a personal lock, keep the key, and post a caution notice at the point of isolation. | Tape over a breaker is not isolation; a multiple-lock hasp where more than one person works on the circuit. | Electrician |
| Prove dead | Prove the voltage indicator on a proving unit, test every conductor at the point of work, then prove the indicator again. | Two-pole voltage indicator to GS38; no multimeters or non-contact testers for proving dead. | Electrician |
| Install or alter | Carry out the work: containment, wiring, accessories and equipment. Shroud or barrier any live parts nearby. | Access equipment chosen by the work at height hierarchy; extraction for chasing; area barriered. | Electricians |
| Inspect and dead test | Inspect the work, then carry out the dead tests, such as continuity and insulation resistance, with the circuit still isolated. | Instruments in calibration; others warned and kept clear before insulation resistance tests. | Tester |
| Energise and live test | When everyone is clear, remove the locks and restore the supply. Then carry out the tests that need it live, such as earth fault loop impedance and RCD tests. | Live tests by competent testers only, with barriers and danger notices; covers back on as soon as possible. | Tester |
| Certify and hand over | Complete the certificate for the work to BS 7671, update circuit charts and labels, and explain the installation to the client. | Results recorded on the schedule of test results; any defects reported in writing. | Supervisor |
| Clear the site | Remove waste cable, offcuts and packaging, take down barriers and hand the area back to the site manager. | No board left open; every circuit left safe and labelled. | Supervisor |

RISK ASSESSMENT

# Hazards, controls and the risk that remains

Each significant hazard rated before and after its controls, as likelihood (1 to 5) times severity (1 to 5). Bands: 1 to 4 low, 5 to 12 medium, 15 to 25 high. The ratings are typical: check them for this site.

| Hazard | Who could be harmed, and how | Risk before | Controls | Risk after | By |
| --- | --- | --- | --- | --- | --- |
| Shock from circuits thought to be dead | Electricians on circuits that are wrongly identified, back-fed, or switched back on by someone else. | 4 x 5 = 20 High | • Circuits identified from drawings, labels and testing, never a label alone, with every source of supply found, including generators and solar inverters. • Isolated at a lockable device with a personal lock and unique key, and a caution notice at the point of isolation. • Proved dead at the point of work with a two-pole voltage indicator, itself proved before and after the test. | 1 x 5 = 5 Medium | Electrician |
| Live working | Electricians testing, fault-finding or working where the supply cannot reasonably be made dead. | 3 x 5 = 15 High | • Live work only where it is unreasonable to work dead, reasonable to work live, and suitable precautions are taken, as EAWR regulation 14 requires. • Each live task justified in writing and authorised before it starts, with insulated tools, shrouding, barriers and suitable PPE. • Where the risk calls for it, a second person trained to recognise danger, switch off and help stays close by. | 1 x 5 = 5 Medium | Supervisor |
| Testing and inspection | Testers, and anyone near a board with its covers off while tests are carried out. | 3 x 5 = 15 High | • Instruments and leads to GS38: CAT rating suited to the installation, finger barriers on probes, and fused leads where the risk assessment calls for them. • Dead tests done first; live tests kept to those that need the supply on. • Covers off only while needed, with the area barriered and a danger notice displayed. | 1 x 5 = 5 Medium | Tester |
| Arc flash and burns at boards and intakes | Electricians working on or beside distribution boards, busbars and supply intakes. | 2 x 5 = 10 Medium | • Work on boards and intakes done dead wherever possible, with the supply side of any isolator treated as live. • Adjacent live parts shrouded or barriered, and danger notices posted on them. • Flame-resistant clothing and face protection where the assessment identifies an arc risk. | 1 x 5 = 5 Medium |  |
| Restoring the supply | Anyone still working on the circuit, and occupants, when the supply is switched back on. | 3 x 5 = 15 High | • Locks removed only by the person who fitted them; a multiple-lock hasp where several people work under one isolation. • Supply restored only after checking that everyone is clear and all tools, earths and covers are removed or refitted. | 1 x 5 = 5 Medium | Electrician |
| Hidden cables in existing buildings | Electricians and other trades drilling or chasing into walls, ceilings and floor voids. | 3 x 5 = 15 High | • Existing services surveyed before work; cables in roof spaces, ceiling voids and floor voids treated as live until proved dead. • Cable detector used before drilling or chasing. Non-contact detectors help find cables but are never used to prove dead. | 2 x 5 = 10 Medium |  |
| Buried cables | Anyone breaking ground for cable runs, earth rods or lighting column bases. | 3 x 5 = 15 High | • Utility drawings checked, then the route scanned with a cable avoidance tool and signal generator by a trained operator, as HSE guidance HSG47 describes. • Cable positions marked on the ground and confirmed by trial holes dug with safe digging methods before any mechanical excavation. | 1 x 5 = 5 Medium |  |
| Overhead power lines | Operatives using ladders, MEWPs or long materials near external overhead lines. | 2 x 5 = 10 Medium | • Overhead lines within 10 metres of the work identified before work starts, as HSE guidance GS6 advises. • Line owner consulted to divert or switch off the line; otherwise barriers and goal posts keep plant and materials at a safe distance. | 1 x 5 = 5 Medium |  |
| Temporary site supplies | Everyone on site using temporary lighting, tools and distribution boards. | 3 x 5 = 15 High | • Temporary system designed and installed by a competent electrical contractor to BS 7671, with 110V centre-tapped earth for lighting and tools where battery tools are not used. • Any 230V socket protected by an RCD, checked daily with its test button. • Distribution system inspected and tested every 3 months, with the records kept on site. | 1 x 5 = 5 Medium |  |
| Asbestos in older buildings | Electricians drilling, chasing or lifting floors in buildings built or refurbished before 2000. | 3 x 5 = 15 High | • Asbestos register or refurbishment survey checked before work; materials not covered by it are presumed to contain asbestos until sampled. • Work stops and the area is left if suspect material is found or disturbed. • Asbestos awareness training for everyone liable to disturb it, repeated at regular intervals. | 1 x 5 = 5 Medium |  |
| Work at height on containment and lighting | Electricians installing tray, trunking, luminaires and cabling at high level. | 3 x 5 = 15 High | • Height avoided where possible, for example by assembling containment runs at ground level. • Podium steps, mobile towers or MEWPs chosen ahead of ladders, with PASMA training for towers and IPAF for MEWPs. • Ladders only for short, low-risk tasks, checked before use and secured. | 1 x 5 = 5 Medium |  |
| Working in occupied buildings | Occupants, staff and the public in homes, offices, schools or shops during the work. | 3 x 4 = 12 Medium | • Supply interruptions agreed with the occupier in advance, with vulnerable occupants and essential equipment identified first. • Work area barriered, open boards never left unattended, and every circuit left safe and labelled at the end of each day. | 1 x 4 = 4 Low |  |
| Dust and noise from chasing and drilling | Electricians chasing walls or drilling masonry, and others nearby. | 4 x 3 = 12 Medium | • Chasing done with on-tool extraction suited to the dust, or a wet method where practicable. • FFP3 or other suitable RPE, face-fit tested, where extraction alone does not control the dust. • Hearing protection where the noise assessment calls for it. | 2 x 3 = 6 Medium |  |
| Manual handling of drums and equipment | Electricians and labourers moving cable drums, boards, switchgear and containment. | 3 x 3 = 9 Medium | • Cable drums run out from drum stands or jacks; heavy boards and switchgear moved on trolleys or with lifting aids. • Long containment lengths carried by two people, on routes kept clear. | 2 x 3 = 6 Medium |  |

MHSWR regulation 3(6): with five or more employees, record the significant findings.

EQUIPMENT

# Plant, equipment and PPE

| Item | Checks and certificates | Operator competence |
| --- | --- | --- |
| Voltage indicator and proving unit | Indicator proved before and after each test; probes and leads to GS38. | Each electrician |
| Multifunction tester | In calibration; leads and probes checked before use. | Competent tester |
| Lock-off kit and caution notices | Personal locks with unique keys; a hasp for multiple locks. | Each electrician |
| 110V tools and transformers | Pre-use check; inspected and tested at the site interval. | Trained user |
| Cable avoidance tool and signal generator | Checked to the maker's instructions before each use. | Trained operator |
| Podium steps, towers and MEWPs | Pre-use checks; towers inspected after erection. | PASMA or IPAF trained |

## Personal protective equipment

PPE is the last line of defence, after the controls above. Specify the type, not just the item.

| Item | Needed | Type and specification |
| --- | --- | --- |
| Safety helmet | Yes | To site standard |
| Safety footwear | Yes | Safety boots with toe protection |
| High-visibility clothing | Yes | To site standard |
| Gloves | Yes | Insulating gloves rated for any live work |
| Eye protection | Yes | For drilling, chasing and cutting |
| Hearing protection | Yes | Where the noise assessment requires it |
| Respiratory protection | Yes | FFP3, face-fit tested, for chasing dust |
| Harness or restraint |  |  |

CONTROLS

# Substances, permits, emergencies and the environment

## Hazardous substances

| Substance | COSHH assessment reference | Controls |
| --- | --- | --- |
| Silica dust from chasing and drilling | COSHH assessment ref | On-tool extraction or wet cutting; FFP3 RPE, face-fit tested |
| Cable lubricants and cleaning solvents | COSHH assessment ref | Use as the safety data sheet directs; gloves; good ventilation |
| Fire-stopping sealants and foams | COSHH assessment ref | Use as the safety data sheet directs; gloves and eye protection |

## Permits and plans

| Permit or plan | Needed | Reference |
| --- | --- | --- |
| Hot work permit | Yes |  |
| Permit to work | Yes |  |
| Permit to dig or break ground | Yes |  |
| Confined space entry |  |  |
| Lift plan |  |  |
| Temporary works design |  |  |

## Emergency and rescue

If someone is in contact with a live conductor, do not touch them until the supply is off. Switch off at the isolator, or break the contact with insulating material. Call 999 and give CPR if trained. First aider and kit on site, and the nearest accident and emergency department named on the briefing.

## Environment and neighbours

Waste cable, metal offcuts and packaging separated for recycling. Lamps and waste electrical equipment kept apart for specialist disposal. Noise from chasing and drilling kept to agreed hours in occupied buildings.

ISOLATION RECORD

# Safe isolation record

One line for each isolation: what was isolated, how it was secured, the proving dead check, and who restored the supply. Keep it with this RAMS until the work is complete.

| Circuit or equipment | Point of isolation and lock number | Isolated by, date and time | Indicator proved, tested dead, re-proved | Restored by, date and time | Notes |
| --- | --- | --- | --- | --- | --- |
| DB2, circuit 7, second floor lighting | DB2 breaker 7, lock-off device, lock 14 | [Name], [date], 08:10 | Yes, at the point of work | [Name], [date], 15:40 | Caution notice fitted |
| Kitchen socket circuit, flat 3 | Consumer unit, RCBO 3, lock 22 | [Name], [date], 09:00 | Yes, all conductors | [Name], [date], 12:30 | Occupier told before restoring |

Electricity at Work Regulations 1989, regulations 12 and 13; HSE HSG85, paragraphs 47 to 56

BRIEFING RECORD

# Briefed before the work starts

Each person signs against this revision, on the day, before starting. Anyone joining later is briefed before they join the work. When the RAMS is revised, everyone is briefed again.

| Briefed by | Revision briefed | Date and time |
| --- | --- | --- |

| Name | Company | Card or ticket number | Signature | Date |
| --- | --- | --- | --- | --- |