[Your logo]

Risk assessment and method statement

# Plumbing and heating RAMS

Plumbing and heating installation and alteration. Pre-filled with typical hazards, controls and sequence: edit it for this site.

Management of Health and Safety at Work Regulations 1999, regulation 3. Gas Safety (Installation and Use) Regulations 1998.

| Detail | Entry |
| --- | --- |
| Project |  |
| Site address |  |
| Activity | Plumbing and heating installation and alteration |
| RAMS reference |  |
| Contractor carrying out the work |  |
| Principal contractor |  |
| Prepared by |  |
| Approved by |  |
| Revision |  |
| Date |  |

Revision record. Reissue and rebrief when the sequence, the programme, the team or the conditions change.

| Rev | Date | What changed | By |
| --- | --- | --- | --- |

THE WORK

# The activity, the place and the people

## Scope of the activity

Installation and alteration of [hot and cold water pipework, heating pipework, radiators, boiler and hot water cylinder] at [address], including draining down, removing old equipment, pressure testing and commissioning. Gas work by Gas Safe registered engineers only. Not included: [list any exclusions].

## Location and access

Access via [entrance], agreed with [occupier or site manager]. Working hours [08:00 to 17:00]. Loft access by [loft ladder or secured ladder], with crawl boards. Materials and old equipment kept at [area]. Water, gas and heating interruptions agreed in advance.

## Interfaces with other trades

Electrician for [boiler and control wiring], and other trades: [trades]. Occupants are told before supplies are isolated or restored. Holes through fire-separating walls and floors are fire-stopped by [trade].

## Documents this RAMS relies on

Drawings or specification [ref]; asbestos register or survey [ref]; manufacturer's installation instructions. Gas Safe registration and ID cards; building control notification or scheme self-certification; commissioning records; hot work permit where required.

## Programme

| Start date | Duration | Working hours |
| --- | --- | --- |

## The team, and their competence

| Role | Name | Card, ticket or training needed | Contact |
| --- | --- | --- | --- |
| Gas engineers |  | On the Gas Safe Register, with the categories on their ID card covering the appliances and the work. |  |
| Unvented systems |  | Competent person scheme registration, or a current skills card for unvented hot water systems. |  |
| Plumbers |  | Trained and experienced in the work, with apprentices and trainees supervised. |  |
| Asbestos |  | Asbestos awareness training, repeated at regular intervals. |  |
| Confined spaces |  | Training for the entry and rescue arrangements wherever a void is a confined space. |  |
| Access equipment |  | Trained in the safe use of ladders and steps, and PASMA for any mobile tower. |  |

METHOD STATEMENT

# The sequence of work

The order the team will work in on the day, with the controls built into each stage. If the sequence changes on site, revise the RAMS and brief it again.

| Stage | What is done, and how | Controls at this stage | By |
| --- | --- | --- | --- |
| Before the day | Survey the property. Confirm the scope, loft and void access, the asbestos information, the isolation points for gas, water and electrics, and whether the work is notifiable. Agree times with the occupier. | Asbestos information checked; Gas Safe categories confirmed for any gas work; RAMS approved by the client or contractor. | Contracts manager |
| Arrival and briefing | Sign in, meet the occupier or site manager, brief the team on this RAMS and agree the work area. Check blowlamps, gas cartridges, test equipment and tools. | Briefing signed against this revision; cards checked; extinguisher on site. | Supervisor |
| Protect the work area | Lay floor protection, clear a route for materials, and move furniture and stored items away from where any soldering will happen. | Walkways kept clear; occupants told which rooms are out of use. | Plumbers |
| Isolate and drain down | Isolate the water, gas and electrical supplies to the parts being worked on. Let the system cool, then drain down into suitable containers or to a drain. | Electrical supply locked off and proved dead; gas isolated and open ends sealed. | Plumbers |
| Remove old equipment | Disconnect and remove old boilers, cylinders, radiators and pipework, draining each item before it is lifted. | Asbestos check before disturbing flues or boards; heavy lifts planned and shared. | Plumbers |
| Install pipework and appliances | Install pipework, fittings, appliances and controls. Solder or braze only where press-fit or push-fit cannot be used, with a heat mat and extinguisher at each joint. | Hot work permit where the site requires one; no dead legs; loft and void access as planned. | Plumbers |
| Pressure and tightness test | Fill and pressure test the water system to the Water Fittings Regulations and the manufacturer's instructions. The gas engineer tests any gas pipework for tightness. | Joints checked before pressurising; others kept clear during the test. | Plumbers |
| Commission | Commission boilers and appliances to the manufacturer's instructions, checking the flue, combustion air, operating pressure or heat input, and safe operation. Set stored hot water to 60°C. | Gas Safe engineer for gas appliances; unvented safety devices checked; system flushed. | Gas engineer |
| Hand over | Show the occupier how to use the system, leave the manufacturer's instructions, and arrange the building regulations notification or self-certification. | Commissioning record completed; any unsafe situation reported to the owner in writing. | Supervisor |
| Clear the site | Remove old equipment, waste and packaging, take up floor protection, and make a last check for heat and leaks before leaving. | Area checked with the occupier or site manager before the team leaves. | Supervisor |

RISK ASSESSMENT

# Hazards, controls and the risk that remains

Each significant hazard rated before and after its controls, as likelihood (1 to 5) times severity (1 to 5). Bands: 1 to 4 low, 5 to 12 medium, 15 to 25 high. The ratings are typical: check them for this site.

| Hazard | Who could be harmed, and how | Risk before | Controls | Risk after | By |
| --- | --- | --- | --- | --- | --- |
| Fire from soldering and brazing | The plumber, occupants and the building, from blowlamp flame near timber, insulation and dust in voids. | 3 x 5 = 15 High | • Press-fit or push-fit fittings used instead of soldering where practicable. • Heat-resistant mat behind every joint, combustibles moved or protected, and an extinguisher within reach. • Hot work permit where the site requires one, with the fire watch it sets. • Area, void and the far side of the wall checked after the last joint, and again before leaving. | 1 x 5 = 5 Medium | Plumber |
| Gas escape, fire or explosion | Engineers, occupants and neighbours when gas pipework or appliances are opened up. | 3 x 5 = 15 High | • Gas work only by Gas Safe registered engineers whose card covers the work, as GSIUR regulation 3 requires. • Supply isolated, open ends sealed with the appropriate fitting, and no source of ignition near exposed gasways. • Gas tightness test immediately after any work that could affect it. | 1 x 5 = 5 Medium | Gas engineer |
| Carbon monoxide from appliances and flues | Occupants and workers, from a blocked, disconnected or poorly installed flue or appliance. | 2 x 5 = 10 Medium | • After work on an appliance, the flue, combustion air supply, operating pressure or heat input, and safe operation are checked. • Any defect reported to the responsible person and the owner, as GSIUR regulation 26(9) requires, and unsafe appliances not left in use. • Flues and appliances installed to the manufacturer's instructions. | 1 x 5 = 5 Medium | Gas engineer |
| Unvented hot water failure | Occupants and plumbers, from stored water overheating or an uncontrolled discharge. | 2 x 5 = 10 Medium | • Installed only by someone with the skills for unvented systems, shown by competent person scheme registration or an unvented skills card. • Factory-fitted temperature and pressure relief valve left in place, with the discharge piped to where it is visible but safe. • Work notified to building control unless self-certified through a competent person scheme. | 1 x 5 = 5 Medium |  |
| Electric shock from boilers, pumps and immersions | Plumbers disconnecting or reconnecting heating controls, pumps and immersion heaters. | 3 x 5 = 15 High | • Electrical supply isolated, locked off and proved dead before work on any appliance or control. • Temporary continuity bond across any cut in metal pipework, and bonding restored before handover. • Electrical connections made by a competent person. | 1 x 5 = 5 Medium |  |
| Scalds and burns | Plumbers draining hot systems, and occupants using outlets after commissioning. | 3 x 3 = 9 Medium | • Systems isolated and left to cool before draining or opening up. • In new dwellings, bath hot water limited to 48°C with a mixing valve, as Part G requires. • Occupants told before hot water comes back on. | 1 x 3 = 3 Low |  |
| Pressure testing | Plumbers and others nearby, if a joint or fitting fails under test pressure. | 2 x 3 = 6 Medium | • Test pressure and method set by the Water Fittings Regulations and the manufacturer's instructions, never exceeded. • Joints checked before pressurising, and others kept clear during the test. • Pump and gauge checked before use; pressure released slowly at the end. | 1 x 3 = 3 Low |  |
| Lifting boilers, cylinders and radiators | Plumbers carrying boilers, cylinders, radiators and baths up stairs and into lofts. | 4 x 3 = 12 Medium | • Avoided where reasonably practicable, then assessed by task, individual, load and environment, as the Manual Handling Operations Regulations require. • Cylinders, boilers and radiators drained before removal; two-person lifts, stair climbers or trolleys for heavy items. • Route checked and cleared before lifting. | 2 x 3 = 6 Medium |  |
| Falls in lofts and roof spaces | Plumbers working on joists, through hatches, and on ladders up to the hatch. | 3 x 4 = 12 Medium | • Crawl boards or boarded walkways across joists; nobody stands on ceiling plasterboard. • Loft ladder or a secured ladder at the hatch, with the opening guarded when people are below. • Temporary lighting in the loft before work starts. | 1 x 4 = 4 Low |  |
| Underfloor voids and confined spaces | Plumbers in underfloor voids, ducts, tanks and chambers with poor air or a difficult way out. | 2 x 5 = 10 Medium | • Entry avoided where the work can be done from outside the space. • Each space assessed; where it is a confined space, entry only under a safe system of work with gas testing and rescue arrangements. • Someone outside always knows who is in the void. | 1 x 5 = 5 Medium |  |
| Asbestos in older properties | Plumbers near pipe lagging, flue pipes, boiler cupboard boards, textured coatings and old cisterns. | 3 x 5 = 15 High | • Asbestos register or refurbishment survey checked before work in buildings built or refurbished before 2000. • Suspect materials presumed to contain asbestos and left undisturbed until sampled. • Asbestos awareness training for every plumber, repeated at regular intervals. | 1 x 5 = 5 Medium |  |
| Legionella in new and altered systems | Occupants and the public, from stagnant or lukewarm water in new, altered or idle pipework. | 2 x 5 = 10 Medium | • No dead legs left in altered pipework; redundant branches cut back to the main run. • Hot water stored at 60°C or above, and cold water kept below 20°C where possible. • Systems flushed, and disinfected where the specification requires, before handover. | 1 x 5 = 5 Medium |  |
| Dust from chasing, drilling and cutting | Plumbers chasing walls, core drilling and cutting masonry for pipe and flue runs, and occupants nearby. | 3 x 4 = 12 Medium | • Pipe routes planned to avoid chasing where practicable, with surface runs or boxing instead. • Chasers and core drills used with water suppression or on-tool extraction to an M or H class unit. • FFP3 RPE, face-fit tested, for dusty work; clean-up by vacuum, never dry sweeping. | 1 x 4 = 4 Low |  |
| Working in occupied homes | Residents, children and visitors in the property while the work is done. | 3 x 4 = 12 Medium | • Water, heating and gas interruptions agreed with the occupier, with vulnerable residents identified first. • Blowlamps, gas cartridges and tools never left unattended. • Floors protected, and hoses and pipes kept out of walkways. | 1 x 4 = 4 Low |  |
| Flooding and water damage | The property and its occupants, from a failed joint or a careless drain-down. | 3 x 2 = 6 Medium | • Stopcock found and checked before work; system isolated and drained into suitable containers or to a drain. • Joints checked under test before floors and boxing are closed up. | 1 x 2 = 2 Low |  |

MHSWR regulation 3(6): with five or more employees, record the significant findings.

EQUIPMENT

# Plant, equipment and PPE

| Item | Checks and certificates | Operator competence |
| --- | --- | --- |
| Blowlamp and gas cartridges | Hose, valve and nozzle checked; cartridges stored away from heat. | Each plumber |
| Press-fit tool | Jaws checked and the tool serviced to the maker's instructions. | Trained user |
| Pressure test pump and gauge | Gauge readable and in good order; valves checked before use. | Plumbers |
| Flue gas analyser and gas pressure gauge | In calibration and checked before use. | Gas Safe engineer |
| Stair climber or trolley | Pre-use check; rated for the load. | Trained user |
| Ladders and crawl boards | Pre-use check; ladder secured at the hatch. | Each plumber |

## Personal protective equipment

PPE is the last line of defence, after the controls above. Specify the type, not just the item.

| Item | Needed | Type and specification |
| --- | --- | --- |
| Safety helmet | Yes | On construction sites, to site standard |
| Safety footwear | Yes | Safety boots with toe protection |
| High-visibility clothing | Yes | On construction sites, to site standard |
| Gloves | Yes | Heat-resistant for soldering, cut-resistant |
| Eye protection | Yes | For soldering, cutting and overhead work |
| Hearing protection |  |  |
| Respiratory protection | Yes | FFP3, face-fit tested, for dusty voids |
| Harness or restraint |  |  |

CONTROLS

# Substances, permits, emergencies and the environment

## Hazardous substances

| Substance | COSHH assessment reference | Controls |
| --- | --- | --- |
| Solder flux | COSHH assessment ref | Use as the safety data sheet directs; gloves; avoid breathing the fume |
| Heating system inhibitor and cleaner | COSHH assessment ref | Gloves and eye protection; spills cleaned up at once |
| Solvent cement and jointing compounds | COSHH assessment ref | Good ventilation; gloves; no flames nearby |
| Loft insulation fibres and dust | COSHH assessment ref | Long sleeves, gloves, FFP3 mask, face-fit tested |

## Permits and plans

| Permit or plan | Needed | Reference |
| --- | --- | --- |
| Hot work permit | Yes |  |
| Permit to work | Yes |  |
| Permit to dig or break ground |  |  |
| Confined space entry | Yes |  |
| Lift plan |  |  |
| Temporary works design |  |  |

## Emergency and rescue

For a smell of gas, turn off the supply at the emergency control, open doors and windows, and use no switches or flames. Call the gas emergency number, 0800 111 999 in Great Britain. For fire, raise the alarm and get out. First aider and kit on site, and the nearest accident and emergency department named on the briefing.

## Environment and neighbours

Old boilers, cylinders, radiators and metal pipe separated for recycling. Drained system water disposed of as the inhibitor safety data sheet directs, never to a surface water drain. Packaging removed from site.

BRIEFING RECORD

# Briefed before the work starts

Each person signs against this revision, on the day, before starting. Anyone joining later is briefed before they join the work. When the RAMS is revised, everyone is briefed again.

| Briefed by | Revision briefed | Date and time |
| --- | --- | --- |

| Name | Company | Card or ticket number | Signature | Date |
| --- | --- | --- | --- | --- |